Lecture 8

CE260/Spring 2000

# Discussion of water, wastes and diseases

- Water quality components and standards

- Chapter 9 Water and wastewater treatment

  - Mass balance and hydraulic flow regimes

    - Applies to many systems

    - SS vs. non SS systems

    - Worst case – best case scenario’s

    - CM completely mixed

    - PF plug flow – transport bulk flow dispersion

  - Word mass balance

In−Out+Generation=Accumulation

# In – Out = net transport across system boundaries

    - Generation = production or destruction

    - Accumulation = amount left over

    - SS vs. concentration in the system

    - Let r = rate of reaction (mass/vol t)

r=±kCn

  - Mass balance for plug flow reactors

Q, C+dCdxΔx

Q, C

1      x        2

A

    - A = cross sectional area

    - If Q = constant and system has 1-D flow

ΔV=AΔx v=QA C=C1+C22

    - Therefore the mass balance is:

In−Out+Generation=AccumulationQC1−QC2+rΔV=dCdtΔVIf at SS then dCdt=0 ∴QC1−QC2+kCnAΔx=0 or QC1−C2ΔV=−r or−dCdΘ=kC or C2=C1r−kΘ

    - Since C1 – C2 = -C if 1st order

−QΔCΔx=kCA

    - Let x  0 and divide by A yields:

QAdCdx=−kC or vdCdx=−kC

    - Since C is only a f(x) then can use total derivative:

v=dxdt dxdtdCdx=−kCdCdt=−kC t=f(x)

  - Determine plug flow reactor (at SS) volume required for 95% removal for a substance as follows:

Ci=150 mgL Q=300 Lhrr=−kC12 k=0.05 hr−1mgL12Ce=1−0.95Ci=7.5mgLQC−QC+dCdxΔx−kC12ΔV=0Reduces to the integralCoCdCC12=−kQ0VdV ⇒ V=2QkCo12−C12V=2300L/hr0.051/hrmg/L1215012mgL−7.512mgL=114 m3

# MB on Completely mixed Reactors

In−Out+Gen=AccumQCo−QC+rV=VdCdtAt SS and first orderQCo−QC−kCV=0Solving for CC=Co1+kΘH td=ΘH=VQDilution rate=1td=QV

V, C

Q, C

Q, Co

    - CM reactors in series

S1

V1

S2

V2

S3

V3

Q, So

    - MB for first two reactors at steady state

QSo−QS1−k1S1V1=0QS1−QS2−k2S2V2=0

    - For the ith reactor:

Si=Si−11+kitdi

    - The influent (So) and effluent (Se) concentrations for n reactors are related by:

SeSo=SnSo=S1So×S2S1×⋯×SnSn−1=11+k1td1×11+k2td2×⋯×11+kntdn

    - If the reactors are identical (Vi/Q = td) and have the same k then:

Se=So1+ktdn=So1+kVnQ

      - V = total volume of all reactors

      - As the # of reactors increase the system approaches plug flow

  - Determine V of CM system for 95% removal

k=(0.05 mgL)12hr−1 Q=300 LhrCi=150 mgL r=−kC12QCo−QC−kC12V=0V=−QCo−QCkC12=312 m3

    - For two CM reactors determine VT where V1 = V2

QCo−QC1−kC112V1=0QC1−QC2−kC212V2=0Solve second MB for C1C1=C2+kC212VQ substQCo−QC2−kC212VQ+kC212V=0QCo−QC2+kC212V+kC212VQ=0

      - Solve the final equation by nonlinear regression analysis or trial and error to get V = 146 m3 therefore VT = 292 m3

      - Compare the three types

        - PF = 114 m3, CM = 312 m3, 2CM = 292 m3

# Flow characteristics in basins

    - Short circuiting

    - Dispersion

    - Measurement of average retention time = V/Q (Figure 10.10)

td=mitimi

  - Flow recycling of CM reactor

r=QrQ tp=VQ+rQ

V

Q + rQ

Q

rQ

Q

    - For an elemental volume q the recycled fraction of that volume is:

rQQ+rQΔq

    - When recycled again a portion stays in for tp

rQQ+rQrQQ+rQΔq=rQQ+rQ2ΔqtT=VQ11+rn=1∞xn−1 when x=r1+r

    - Read over example 10.4 in text