Lecture 9

CE260/Spring 2000

# Physical Chemical Treatment

  - Particle removal process

    - Screens and bar racks

    - Type I, II, and III sedimentation

    - Grit chambers

  - Oxygen mass transfer

  - Coagulation & flocculation

  - Filtration

  - Water softening (remove hardness)

  - Ion exchange

  - Membrane process

  - Activated carbon

  - Disinfection

# Screens and bar racks

# Intakes from rivers, lakes, and reservoirs for water treatment plant

  - Sewer inlet to plants

  - Protect pumps in pumping station

    - Coarse 	50 – 150 mm

    - Medium 	20 – 50 mm

    - Fine 	<10mm

    - Don’t want something in front of these, will block flow (Vmin = 0.6 m/s)

VSe

h2

h

h1

  - Bernoulli’s equation used for headloss calculations

h1+V22g=h2+VSe22g+losses

    - Can use friction factor, Cd to describe losses

Δh=h1−h2=12gCd2VSe2−V2Typically Cd=0.84

    - Can use orifice equation for velocity through screen

Δh=VSe22gCd2=12gQCdA2

    - Mechanically cleaned screens, get Cd from manufacturer

    - Manually cleaned screen need Ad = 0.05 Aactual

    - Quantities of screens and disposal must be considered

      - Water treatment 1.3 mm openings – 0.29L/1000 m3 of Q

      - WWTP 50 to 150 mm screens at inlet with bar racks, 25 mm for other parts of the plant (see table 11.1 for estimates of WWTP)

      - 3.5 to 35 L/1000 m3

      - solids content 640-1100 kg/m3

      - b = 40 – 70 lb/ft3

      - %VS = 75 – 95%

      - Fuel value – 12,600 kJ/kg (5,400 Btu/lb)

  - Microstrainers – usually rotating drum with fabric (Fig. 11.4)

    - Design Parameters

      - Mesh size 20 – 25 um

      - Hydraulic loading 12 – 24 m3/m2 hr

      - Max hL 30 – 45 cm

      - Peripheral drum speed 4.5 m/min at 7.5 cm hL

      - Wash water at 2 – 5%

      - Secondary effluent w/ TSS 6 – 65 mg/L, removal 43 – 85%

      - Can be used for stormwater and algae removal

## Sedimentation

  - Type I

    - Assumptions

      - Discrete particle

      - Infinite size vessel

      - Viscous fluid

      - Single particle

      - Quiescent fluid

    - Bassett’s 1888 eq. for force balance for terminal velocity

### Change in momentum = particle weight – buoyant force – drag force

ma=Fg+Fb+Fd−ρpVpdVdt=ρpVpg−ρwVpg+12CDApVs2

    - When particle reaches terminal V dV/dt = 0, rearrange

Vs=2gCDVpAPρp−ρwρwfor spherical particleVs=43VpAPρp−ρwρwCD=fRe for Re=ρVdμ

CD=24Re for Re<1 laminar flow24Re+3Re12+0.34 trans. flow 1<Re<103

    - Type I settling tank typical equations

t=VQ Vf=QBH votd=H vftd=LLvf=Hvo and vo=vfHL=QBL=QAs

    - Sedimentation designs theoretically  f(H)

If upflow sedimentation basin Vf Q/As

Vf

    - If vf = vo then all particles w/ v  vo will be removed

    - If v  vo then particle will pass by

    - If horizontal flow some particles with v < vo will be removed, if they enter at h < H

    - Assume particle w/ v < vo will travel a vertical distance h in one td

    - All particles with settling v are uniformly distributed in inlet zone

h=vtd hH≤vvor=hH=vvo

    - Can be shown that the R = fraction by weight of all different sized particles removed is the sum of individual particle sizes removed

    - Figure 11.7 is a settling velocity curve for a suspension

R=1−po+riR=1−po+vo+v12vopo−p1+v1+v22v0p1−p2+⋯limit is: R=1−po+1vo0povdp

      - To solve for R use a polynomial fit or graphic interpolation (as in Fig. 11.7)

    - For circular tanks w/ inlet in middle and radial flow

vo=QAs r=hH=vvo

  - Type II sedimentation

    - Some agglomeration usually with natural or man made chemical agents

    - Flocculant type settling (Fig. 11.9 graph of settling trajectory)

    - Test for flocculation (jar tests) use columns to measure settling

    - Examples of data obtained during flocculation test w/ Co = 430 mg/L

| Raw Data | Concentration mg/L |  |  |
| --- | --- | --- | --- |
| Time (min) | 60 cm | 120 cm | 180 cm |
| 5 | 357 | 387 | 396 |
| 10 | 310 | 346 | 366 |

| Raw Data | Solids Removed % |  |  |
| --- | --- | --- | --- |
| Time (min) | 60 cm | 120 cm | 180 cm |
| 5 | 17.0 | 10.0 | 7.9 |
| 10 | 28 | 19.5 | 14.5 |

    - Figure 11.12 is the percent solids removed at each depth, which can be easily used to interpolate the solids removed at any depth

| Interpolated | t, min |  |  |
| --- | --- | --- | --- |
| % SS removed | 60 cm | 120 cm | 180 cm |
| 5 | 1.2 | 2.5 | 3.7 |
| 10 | 2.5 | 5.0 | 6.5 |

    - Figure 11.13 shows the isoconcentration curves

    - Fraction removed

ri=diDΔpi or vivo=diD

      - di = average depth reached by the ith fraction

      - D = effective settling depth

      - vi = average settling velocity of the ith fraction

      - At time 45 min (book is wrong) from Figure 11.13 % removed is:

Δpi=50−40dSS% removed=130cmD=180cm

13018050−40=7.27818060−50=4.34818070−60=2.77018075−70=0.8

R=ro+ri=40+7.2+4.3+2.7+0.8=55%

    - The next step is to create a figure of R vs t

      - Must consider increase of R at cost of obtaining t

      - Compare to other removal processes

      - Sizing of basin consider safety factors

        - Multiply design td based on column performance by 1.25 – 1.75

        - Divide design Q/A based on column performance by 1.25 – 1.75

      - Can use tube or lamella clarifiers

  - Type III sedimentation – zone settling, hindered settling

    - Generally w/ TSS > 500 mg/L in flocculation suspension (Figure 11.21 progression of zone sedimentation)

    - If t is to great will get anaerobic condition release CH4 and CO2

    - Can use 2 L graduated cylinder to gather data for zone sedimentation

    - Generally design clarifiers to settle TSS out from clarified effluent and thicken sludge (Figure 11.23)

    - Interface settling rate for type III sedimentation

N=−vC

      - N = solids flux

      - v = interface volume in the tank occupied by sludge

      - C = concentration of the suspension

    - Design of Type III settlers

      - Figure 11.27 give the preliminary plots for gravity flux determination

Ng=Civh

      - Ci = initial concentration of the suspension

      - Look at Figure 11.28 which represent the mass flux from gravity

      - Vesiland equation used to describe settling velocity of a suspension at any concentration

vh=ae−bC

      - Years later Wahlberg and Keinath defined a and b as follows:

vh=5.3−0.061SVIe−0.426+0.00384SVI−0.0000543SVI2C

      - Underflow flux in addition to gravity solid flux

        - Underflow increases downward movement of solids

Ub=QuAs=underflow velocityNu=CUb=underflow solids flux

      - Total solids flux = N

N=Ng+Nu=Cvh+CUb

      - Figure 11.29 Total mass flux as a f(conc)

As≥QCoN=solids loadingtotal solids flux

      - All solids are removed by bulk flow (underflow)

CuQu=QCo=AsNL

  - Other important issues for sedimentation

    - Weir – design and geometry – important to have minimum velocity of water over the weir

    - Launder design channel for transient flow don’t want to flood launder

  - Basic properties

    - Water treatment

      - Depth 2.4 – 4.9 m, SOR 20 – 70 m2/m3-day

    - WWTP

      - Primary – depth 2.1 – 5 m, avg. Q 32 – 49 m3/m2-day, peak 49 – 122 m3/m2-day

      - Secondary - depth 3.0 – 5.0 m, avg. Q 16 – 29 m3/m2-day, peak 41 – 65 m3/m2-day