Lecture 11

- Filtration

  - Coag-floc-settling-filtration produces H20 with very low turbidity.

  - Filtration removes bacteria very well

  - Filtration affective for spore and cysts associated with Cryptosporidium and Giardia

  - SAND is most common media

  - Crushed anthracite and inert materials also used

    - Removal is  f(A particles)

    - 1 m3 filter, 0.4 = N + 0.5mm dia. Particles

    - 9.17e9 particles

    - w/ 7.2e3m2/m3

    - may only have very small % effective A

    - still a large number

Variety of filtration mechanisms exist

  - Slow Sand Filters

    - Includes microbial gelatenous growth during ripening stage

    - This layer removes most particles

    - As hL increases, then scrape off top

  - Rapid Sand Filters

    - Uses entire depth

    - High loading

    - More rapid hL build-up

    - Backwash

      - Scour and shear forces

      - Particle segregation

        - Need relatively uniform material

  - e, porosity is important

  - Sphericity

ψ=AsphereVsphereApartVpart

  - Substituting for spherical geometry

ψ=6Πd2Πd3VpApwhere Vp=VsApVp=6ψd

  - Grain size distribution and uniformity

  - Effective Size = ES = P10 – tenth particle in value

  - Uniformity coefficient – U = P60/P10

    - P = wt fraction  size

    - d10, d60, and d90 are used in design

    - Can use backwash to make media more uniform

  - Headloss is important in rapid and slow sand filters

    - Darcy Weisbach equation

hL=fLDV22g

    - Replace D with R (hydraulic radius)

R=areawetted perimeter

    - For a circular section

R=πD24πD=D4

    - Substitute into Darcy Weisbach equation

hL=fLv28gR

    - R for filter media is not well defined

R=areaWP≈Volume avail for flowtotal SA. of particlesVTP=NVP ATP=NAPe=void volumefilter volume 1−e=volume particlesfilter volume

ff=1501−eRe+k k≈1.75Re=ρvsdμ=ρvsϕdμ

    - Substitute back into the Darcy Weisbach eq.

hLL=150μρg1−e2e3vsψd2+k1−ee3vs2ψdg

    - Left hand side of the eq. Represents laminar flow and the right hand side represents turbulent flow

    - L is the depth of the filter

    - Usually when hL ~ 1.5 o 2.0 m backwashing will occur