Lecture 12

CE260/Spring 2000

- Physical chemical treatment

  - Water softening = removal of certain dissolved minerals - cause scaling on pipes - excessive use of soaps

  - Iron and manganese removal

  - Membrane processes

  - Adsorption

  - Disinfection/oxidation

- Water softening

  - Hardness - scaling, taste, color, impurities for industrial uses

    - Generally due to Ca2+, Mg2+ divalent Me2+

    - Total hardness = calcium hardness + magnesium hardness

    - Major cations

      - Ca2+, Mg2+, Na+, and K+

    - Major anions

      - HCO3-, CO32-, OH-, Cl-, SO42-, and NO3-

    - Because Ca2+ is predominant hardness cation hardness is expressed as CaCO3 (GMW = 100, Eq. Wt. = 50)

      - Soft water < 60mg/l as CaCO3

      - Moderately hard 60 - 120

      - Hard 120 -180

      - Very hard >180

  - Lime Soda softening

HCO3−+OH−↔CO32−+H2O if ↑pHHCO3−↔CO32−+Ca2+→CaCO3(s)

    - Slaked lime Ca(OH)2 usually used (hydrated lime) CaO (quicklime) , NaOH (caustic soda)

    - If HCO3- is insufficient then add Na2CO3 (soda ash)

    - Relevant reactions

Ca(OH)2+CO2→CaCO3(s)+H2OCa(HCO3)2+Ca(OH)2→2CaCO3(s)+2H2OMg(HCO3)2+Ca(OH)2→CaCO3(s)+MgCO3+2H2OMgCO3+Ca(OH)2→CaCO3(s)+Mg(OH)3(s)

    - Need pH > 10.5 because pKa ~10.3

    - Temperature will effect the rates of rxn and equilibrium Ca2+ and Mg2+ concentrations

    - Ca2+ ~ 20 to 30 mg/L can be achieved

    - Mg2+ ~ 10 mg/L can be achieved

    - Figure 15.2 represents a split treatment diagram for hardness removal

    - The final Mg2+ concentration dictates the fraction of flow bypassed

(1−x)Q[Mg]1+xQ[Mg]o=Q[Mg]f

- Use of Bar Graphs

| Constituents | Conc. (mg/L) | Eq. Weight | Eq. Conc. (meq/L) |
| --- | --- | --- | --- |
| CO2 | 9.5 | 22 | 0.43 |
| Ca2+ | 98 | 20 | 4.90 |
| Mg2+ | 27 | 12.2 | 2.20 |
| Na+ | 6.5 | 23 | 0.28 |
| HCO3- | 281 | 61 | 4.6 |
| SO42- | 120 | 48 | 2.5 |
| Cl- | 6.1 | 35.5 | 0.18 |

Ca(OH)2=CO2+Ca(HCO3)2+Mg2++excess lime (1.25 meqL)Ca(OH)2=0.43+4.6+2.20+1.25=8.48 meqL

  - See Figure 15.3 for the bar graphs

- Lime recovery by heating sludge

  - If primary sedimentation precedes softening then CaCO3 and MgOH2 are the only solids:

CaCO3heatCaO+CO2(g)→atm

- Chemical stabilization of water

  - Should not be corrosive

  - Adjust pH, [Ca2+], and alkalinity to be CaCO3 equivalents

  - Preserves a film of CaCO3(s) on pipes

  - Stable if neither precipitate or dissolution of CaCO3(s) occur

  - Equations used to calculate the pH required to precipitate CaCO3(s)

Ca2++CO32−↔CaCO3(s) 1KspHCO3−↔H++CO32− K2Ca2++HCO3−↔H++CaCO3(s)

Ksp=γCa2+[Ca2+]γCO32−[CO32−]K2=γH+[H+]γCO32−[CO32−]γHCO3−[HCO3−]K=KspK2=γCa2+[Ca2+]γHCO3−[HCO3−]γH+[H+]pHmeter=−logγH+[H+]

    - If we let pH = pHs (saturation pH of CaCO3)

pHs=−logγH+[H+]=logK−logγCa2+[Ca2+]−logγHCO3−[HCO3−]pHs=logKsp−logK2−log[Ca2+]−log[HCO3−]−logγCa2+γHCO3−

    - Using p notation

pHs=pK2−pKsp−log[Ca2+]+S−log[alkalinity] orpHs=pK2−pKsp+p[HCO3−]−logγCa2+−logγHCO3−

    - S = salinity correction factor

    - Need to apply at the current temperature of the water see Table 15.4

    - If pH < pHs could have corrosion

    - If pH > pHs could have deposition

    - Langelier index (1936)

SI=pH−pH