Lecture 14

CE260/Spring 2000

- Aerobic biological treatment

  - Remove dissolved and colloidal material

    - Transform chemicals into less harmful state

  - Bacteria are primary agents

    - Some higher organisms protozoa, yeast and fungi

    - Dissolved oxygen in biomass may be quite low

    - Can result in facultative bacteria

  - Activated sludge process

    - Mixed aeration basins - diffused air or impeller mix

    - Biomass culture is called mixed liquor

  - CFSTR (Figure 17.1)

    - Microbes use substrate for mass and energy

    - Results in lots of sludge to waste

    - Cost of sludge processing/disposal

    - Quality of sludge industrial/municipal metals

  - Substrate removal and growth of biomass

    - Recall the Monod equation

μ=μmaxSKs+S

  - VSS - Volatile suspended solids

    - Used as a surrogate to estimate active biomass - endogenous decay factors in so active biomass < VSS

    - MLVSS

    - Could use ATP but not practical from routine plant operations

  - Temperature impacts of growth

    - Recall Arrhenius equation

kT=k20θT−20

    - 1 <  < 1.8, for activated sludge  ~ 1.04

  - Growth of microbes and sludge production

rxp=−yrs rs=−kSK+S

    - rxp = production of VSS from substrate removal

    - y = yield factor (mg VSS prod/mg substrate removed)

    - system produces low BOD so we are in substrate limited mode therefore, the biomass is degrading itself

    - rxe = endogenous decay rate (mg VSS/L-day)

rxe=−keXv

    - Thus the net growth rate rx:

rx=−yrs−keXv

    - Typical values

      - Y = 0.4 to 0.84 typically ~0.6

      - ke = 0.004 to 0.10 typically ~0.06

    - Can combine rx = yobsrs

    - Sludge composition - cells type C5H7NO2 and C5H7NO2P0.074

    - Most typical CMSTR (Figure 17.3)

XTO=XTiO+XVO

    - XTO = TSS

    - XTiO = inert TSS

    - XVO = VSS

    - Xa = active biomass

    - Food:microorganiam ratio (F:M) = U

U=Q(So−Se)XvV=So−SeXvθd

    - d = hydraulic retention time

    - Since Se << So U can be approximated by:

U=SoXvθd

    - Sludge age x = mass solids in aeration basin/solids removal rate

θx=XvVθwXVr

  - SVI - sludge volume index

    - Measure of settleability and compatibility

    - Method

      - Settling column = 1-2 L, after time = 0.5hr to 1hr

      - Measure volume of space occupied by 1gram of VSS

SVI (mLg)=yXT(1000 mgg)

      - Low SVI sludge settles well, can estimate conc. of VSS and TSS in the recycle line

XTr=106SVI XVr=XVXTXTr

  - CMSTR w/ recycle

    - Biomass mass balance

QXVo−QXVr−(Q−Qw)Xve+rxV=dXVdt

    - At steady state V=0

    - If XVo << XVr  XVe then:

QwXVr+(Q−Qw)XVe=rxV

    - Define sludge age (x) mean cell residence time and also T = residence time of sludge in entire system

θx=XVV(Q−Qw)XVe+QwXVrθT=XVV+XVcVcQwXVr+(Q−Qw)XVe1θx=y(So−Se)XVθd−keXV=θxθd=y(So−Se)1+keθx

    - Frequently the range is x > 10xd

    - ke = endogenous decay rate

  - Recycle rate

    - Designer controls HRT and SRT in system, operator varies within design parameters

    - Consider mass balance cell around classifier

Q(1+r)XV=(Q−Qw)XVe+rQXVr+QwXVrVXVθx=(Q−Qw)XVe+QwXVr(1+r)XV=VXVQθx+rXVr1θx=QV1+r−rXVrXV

    - XVr/XV = measure of compatibility of sludge

    - Solve the above equation for the sludge recycle r:

r=1−θdθxXVrXV−1

    - Substrate mass balance

QSo−QSe+rsV=dSeVdt=0 at SSrs=−Q(So−Se)V=−So−Seθd

    - If Monod is substituted for rs

−kSeKs+Se=−So−SeθdSe2−kSeθd−SoSe+KSe−KSo=0Se=−b+b2−4ac2ab=kθd−So+K c=−KSo a=1

  - Determination of parameters for an activated sludge process (example 17.1)

    - Rearrange eq. 17.15 to the linear Lineweaver Burke form:

XVρ=XVθdSo−Se=Kk1Se+1k

    - Follow the example o find parameters x, d, So, Se and XV